## RF Channel Map
REACH / XPander RF Map
When installing a REACH Wireless system within the wireless vicinity of each other, it is important to ensure that both systems are: 1. Operating on different RF Frequencies 2. Maintaining a 0.05Mhz gap between each other (1) should be the case for any RF wireless system install, including REACH-only or XPander-only systems. (2) is required to prevent communication issues with XPander systems and is required for XPander-only or XPander/REACH mix systems. REACH-only installations only need to be set to different channel pairs. This document will aid in the frequency/channel selection process if a REACH or XPander wireless system is already installed.
Key |  | Both REACH and XPander systems are configured with Primary and Secondary (backup) RF communication channels. For REACH systems, these are pre-defined pairs, whereas XPander can be any Primary channel 1-16 paired with any Secondary 17-32.
REACH
XPander
Delta
RF Frequency by stated channel number |  |  |  | RF channel by frequency order |  |  |  | RF Channel A/B by pair
Channel No. | REACH Frequency | Channel No. | XPander Frequency | REACH/XPander Frequency | Delta | Channel No. |  | REACH Channel Pair No. | REACH Channel No. | REACH Frequency | XPander Channel No. | XPander Frequency | Delta
1 | 868.0125 | 1 | 868.048 | 868.0125 |  | 1 | Channel A | 1 | 55 | 869.7125 | 1 | 868.048 | 1.6645
2 | 868.0375 | 2 | 868.073 | 868.0375 | 0.025 | 2 |  | 2 | 56 | 869.7375 | 2 | 868.073 | 1.6645
3 | 868.0625 | 3 | 868.098 | 868.048 | 0.0105 | 1 |  | 3 | 57 | 869.7625 | 3 | 868.098 | 1.6645
4 | 868.0875 | 4 | 868.123 | 868.0625 | 0.0145 | 3 |  | 4 | 58 | 869.7875 | 4 | 868.123 | 1.6645
5 | 868.1125 | 5 | 868.148 | 868.073 | 0.0105 | 2 |  | 5 | 59 | 869.8125 | 5 | 868.148 | 1.6645
6 | 868.1375 | 6 | 868.173 | 868.0875 | 0.0145 | 4 |  | 6 | 60 | 869.8375 | 6 | 868.173 | 1.6645
7 | 868.1625 | 7 | 868.198 | 868.098 | 0.0105 | 3 |  | 7 | 61 | 869.8625 | 7 | 868.198 | 1.6645
8 | 868.1875 | 8 | 868.223 | 868.1125 | 0.0145 | 5 |  | 8 | 62 | 869.8875 | 8 | 868.223 | 1.6645
9 | - | 9 | 868.248 | 868.123 | 0.0105 | 4 |  | 9 | 63 | 869.9125 | 9 | 868.248 | 1.6645
10 | - | 10 | 868.273 | 868.1375 | 0.0145 | 6 |  | 10 | 64 | 869.9375 | 10 | 868.273 | 1.6645
11 | - | 11 | 868.298 | 868.148 | 0.0105 | 5 |  | 11 | 65 | 869.9625 | 11 | 868.298 | 1.6645
12 | - | 12 | 868.323 | 868.1625 | 0.0145 | 7 |  | 12 | 66 | 869.9875 | 12 | 868.323 | 1.6645
13 | - | 13 | 868.349 | 868.173 | 0.0105 | 6 |  | 13 | 1 | 868.0125 | 13 | 868.349 | -0.3365
14 | - | 14 | 868.374 | 868.1875 | 0.0145 | 8 |  | 14 | 2 | 868.0375 | 14 | 868.374 | -0.3365
15 | - | 15 | 868.399 | 868.198 | 0.0105 | 7 |  | 15 | 3 | 868.0625 | 15 | 868.399 | -0.3365
16 | - | 16 | 868.424 | 868.223 | 0.025 | 8 |  | 16 | 4 | 868.0875 | 16 | 868.424 | -0.3365
17 | 868.4125 | 17 | 868.479 | 868.248 | 0.025 | 9 |  | 17 | 5 | 868.1125
18 | 868.4375 | 18 | 868.774 | 868.273 | 0.025 | 10 |  | 18 | 6 | 868.1375
19 | - | 19 | 868.8 | 868.298 | 0.025 | 11 |  | 19 | 7 | 868.1625
20 | - | 20 | 868.825 | 868.323 | 0.025 | 12 |  | 20 | 8 | 868.1875
21 | - | 21 | 868.85 | 868.349 | 0.026 | 13 |  | 21 | 17 | 868.4125
22 | - | 22 | 868.875 | 868.374 | 0.025 | 14 |  | 22 | 18 | 868.4375
23 | - | 23 | 868.9 | 868.399 | 0.025 | 15
24 | - | 24 | 868.925 | 868.4125 | 0.0135 | 17 | Channel B | 1 | 25 | 868.7125 | 1 | 868.048 | 0.6645
25 | 868.7125 | 25 | 868.95 | 868.424 | 0.0115 | 16 |  | 2 | 26 | 868.7375 | 2 | 868.073 | 0.6645
26 | 868.7375 | 26 | 868.975 | 868.4375 | 0.0135 | 18 |  | 3 | 27 | 868.7625 | 3 | 868.098 | 0.6645
27 | 868.7625 | 27 | 869 | 868.479 | 0.0415 | 17 |  | 4 | 28 | 868.7875 | 4 | 868.123 | 0.6645
28 | 868.7875 | 28 | 869.025 | 868.7125 | 0.2335 | 25 |  | 5 | 29 | 868.8125 | 5 | 868.148 | 0.6645
29 | 868.8125 | 29 | 869.05 | 868.7375 | 0.025 | 26 |  | 6 | 30 | 868.8375 | 6 | 868.173 | 0.6645
30 | 868.8375 | 30 | 869.075 | 868.7625 | 0.025 | 27 |  | 7 | 31 | 868.8625 | 7 | 868.198 | 0.6645
31 | 868.8625 | 31 | 869.1 | 868.774 | 0.0115 | 18 |  | 8 | 32 | 868.8875 | 8 | 868.223 | 0.6645
32 | 868.8875 | 32 | 869.125 | 868.7875 | 0.0135 | 28 |  | 9 | 33 | 868.9125 | 9 | 868.248 | 0.6645
33 | 868.9125 | 33 | - | 868.8 | 0.0125 | 19 |  | 10 | 34 | 868.9375 | 10 | 868.273 | 0.6645
34 | 868.9375 | 34 | - | 868.8125 | 0.0125 | 29 |  | 11 | 35 | 868.9625 | 11 | 868.298 | 0.6645
35 | 868.9625 | 35 | - | 868.825 | 0.0125 | 20 |  | 12 | 36 | 868.9875 | 12 | 868.323 | 0.6645
36 | 868.9875 | 36 | - | 868.8375 | 0.0125 | 30 |  | 13 | 37 | 869.0125 | 13 | 868.349 | 0.6635
37 | 869.0125 | 37 | - | 868.85 | 0.0125 | 21 |  | 14 | 38 | 869.0375 | 14 | 868.374 | 0.6635
38 | 869.0375 | 38 | - | 868.8625 | 0.0125 | 31 |  | 15 | 39 | 869.0625 | 15 | 868.399 | 0.6635
39 | 869.0625 | 39 | - | 868.875 | 0.0125 | 22 |  | 16 | 40 | 869.0875 | 16 | 868.424 | 0.6635
40 | 869.0875 | 40 | - | 868.8875 | 0.0125 | 32 |  | 17 | 41 | 869.1125
41 | 869.1125 | 41 | - | 868.9 | 0.0125 | 23 |  | 18 | 42 | 869.1375
42 | 869.1375 | 42 | - | 868.9125 | 0.0125 | 33 |  | 19 | 43 | 869.1625
43 | 869.1625 | 43 | - | 868.925 | 0.0125 | 24 |  | 20 | 44 | 869.1875
44 | 869.1875 | 44 | - | 868.9375 | 0.0125 | 34 |  | 21 | 53 | 869.6125
53 | 869.6125 | 53 | - | 868.95 | 0.0125 | 25 |  | 22 | 54 | 869.6375
54 | 869.6375 | 54 | - | 868.9625 | 0.0125 | 35
55 | 869.7125 |  |  | 868.975 | 0.0125 | 26
56 | 869.7375 |  |  | 868.9875 | 0.0125 | 36
57 | 869.7625 |  |  | 869 | 0.0125 | 27
58 | 869.7875 |  |  | 869.0125 | 0.0125 | 37
59 | 869.8125 |  |  | 869.025 | 0.0125 | 28
60 | 869.8375 |  |  | 869.0375 | 0.0125 | 38
61 | 869.8625 |  |  | 869.05 | 0.0125 | 29
62 | 869.8875 |  |  | 869.0625 | 0.0125 | 39
63 | 869.9125 |  |  | 869.075 | 0.0125 | 30
64 | 869.9375 |  |  | 869.0875 | 0.0125 | 40
65 | 869.9625 |  |  | 869.1 | 0.0125 | 31
66 | 869.9875 |  |  | 869.1125 | 0.0125 | 41
|  |  |  | 869.125 | 0.0125 | 32
|  |  |  | 869.1375 | 0.0125 | 42
|  |  |  | 869.1625 | 0.025 | 43
|  |  |  | 869.1875 | 0.025 | 44
|  |  |  | 869.6125 | 0.425 | 53
|  |  |  | 869.6375 | 0.025 | 54
|  |  |  | 869.7125 | 0.075 | 55
|  |  |  | 869.7375 | 0.025 | 56
|  |  |  | 869.7625 | 0.025 | 57
|  |  |  | 869.7875 | 0.025 | 58
|  |  |  | 869.8125 | 0.025 | 59
|  |  |  | 869.8375 | 0.025 | 60
|  |  |  | 869.8625 | 0.025 | 61
|  |  |  | 869.8875 | 0.025 | 62
|  |  |  | 869.9125 | 0.025 | 63
|  |  |  | 869.9375 | 0.025 | 64
|  |  |  | 869.9625 | 0.025 | 65
|  |  |  | 869.9875 | 0.025 | 66